## Slide 1
Energy Efficient Retrofit Strategies towards nZE Preschool Building in Malaysia
ICARB 2023
Measuring Net Zero
Dr. Norhayati Mahyuddin, PhD
Associate Professor, Faculty of Built Environment, Universiti Malaya
Sep 2023

## Slide 2
Introduction
Method
Results
Conclusion
Outline
National action plans for net zero carbon in 2050
nZEB definition & retrofit challenges in Malaysia
Energy performance audit & monitoring
Energy performance simulation - EE assessment
Retrofit alternatives implementation & potential energy savings
Summary & Future work
01

## Slide 3
Global operational energy demand in buildings from 2020
Global operational CO2 emissions from 2020
4%
D
5%
C
14%
B
53%
A
Total energy consumption in building sector in Malaysia
Total electricity consumption in commercial & residential
Malaysia’s per capita CO2 emissions are rising to about 8t PCPA and categorized as being above the upper middle-income countries at 6.6t PCPA
Introduction
02

## Slide 4
Introduction
National action plans - 2050
12th Malaysia Plan (2021-2025)
To be carbon neutral as early as 2050; 45% reduction in GHG emissions intensity to GDP by 2030
National Energy Policy (2022-2040)
EE savings by non-residential by 11% by 2040
Kuala Lumpur Climate Action Plan 2050 (2021-2026)
To reduce energy consumption of buildings through technical specifications; To develop maximum allowable Building Energy Intensities to support increased EE; To develop a roadmap with strategies across the lifecycle of buildings to reduce GHG emissions have been prioritized
Towards Zero Carbon
Green Technology Master Plan (2017-2030)
To achieve a nZEB scenario by 2040
By improving EE in the building and transport sectors, RM 46.9 billion (USD 11.2 billion) could be saved between 2016 and 2030 in Malaysia
(Lee, 2019)
03

## Slide 5
nZEB definition
nZEB retrofit challenges in Malaysia
Hot and humid conditions - as a norm
Lack of sufficient awareness among the local stakeholders - effective implementation and performance
Adoption of RE technology is not commercially viable yet - lack of experience and suitable support mechanisms in the market environment
EE investment has been regarded as risky and costly by public and building owners
Introduction
nZEB Measures
03
To provide on-site renewable energy generation to supply and counter-balance the residual energy demand of the building
To optimize passive measures:
01
envelope insulation, solar heat gain, daylight harvesting, airtight envelope, natural ventilation
02
To minimize active measures:
HVAC, lighting, electrical appliances
Malaysia adopted the Japanese definition of nZEB with minor changes based on the climate conditions and country building standards:
Buildings that realize reduction of primary energy consumption by 75% with energy saving (50% or more) and energy creation (~ 25% residual)
Active measures
50% reduction
04

## Slide 6
To address the gap, an existing preschool building (TADIKUM) at the campus of Universiti Malaya was selected for nZEB refurbishment
Aims to facilitate the widespread adoption of the nZEB retrofit strategies, for existing school buildings, as a norm concept in tropical climate regions to reduce the impact that our buildings have on contributing to climate change
Introduction
Easy-to-install
EE design strategies’ considerations & limitations
Preschools
Total schools
36,249
25,200
Simple
Do not affect the daily activities in the school
Working with the budget
TADIKUM BUILDING
TADIKUM was constructed in 1984 as a double-storey residential building; a change of use to educational in 2014
05

## Slide 7
Retrofit alternatives implementation & potential energy savings
Energy performance audit & monitoring
Energy performance simulation - EE assessment
01
02
03
Method
Onion model approach in implementing EE strategies
Electricity consumption (kWh) of:
AC
Lighting
Plug Load - Appliances
Location / orientation
Building envelope
Electricity bills
AC system
Lighting fixtures
Model calibration
EE initiatives
1 2 3 4 5 6 7 8 9
Add roof insulation
Seal air vent louvered windows
Daylight harvesting
Energy Efficient lights
Small Power improvements
Solar film on all windows
Replacing AC with high COP
Replacing AC with highest COP
Heat Recovery Wheel for fresh air intake
Optimized nZEB
Research method diagram
06

## Slide 8
Results
Lighting (Fluorescent T8 - 36W) | 42
Air conditioner (1 HP - 9,500 Btu/h) | 5
Air conditioner (2.5 HP - 21,000 Btu/h) | 4
Ceiling Fan | 10
Air Purifier | 9
Computer | 7
Projector & TV | 1
Fridge | 1
Freezer | 1
Hot/Cold Water Dispenser | 1
Rice Cooker | 2
Printer/Copy/Scanner | 1
Water Heater | 4
Occupancy | 88
TADIKUM East-North view
Daily operating hours: 10.00 a.m. to 4.30 p.m.
1. Energy performance audit & monitoring
Optimal orientation in tropical climate: North-South
TADIKUM orientation: East-West
Inevitable fenestrations on east (13% WWR) and west (15% WWR) facades
Higher heat conductivity through walls & windows; higher solar heat gain through windows; glare discomfort in classrooms
Poorly sealed horizontal louvre windows on the west façade
High rate of air infiltration and poor thermal efficiency
Inadequate portion of openings on the North façade (12% WWR)
Full-day dependency on artificial lighting
Large windows on the south façade (45% WWR) without proper shadings
Excessive heat conductivity, solar heat gain, glare discomfort
Glazing type 6mm clear glass
High U-Value of 5.82 W/m2K; Major contributor to solar heat gain and heat conductivity through the windows
Appliances
High SHGC
High WWR
Increase in solar heat gain ratio, cooling load of the building, and electricity consumption
Scope
07

## Slide 9
Results
2. Energy performance simulation - EE assessment
Prerequisites criteria | EE design considerations & strategies |  |  |  | 
SHGC | The most EE factor to consider in hot and humid climate Reduction of the glazing area is not possible to decrease the high rate of WWR in TADIKUM, thus reducing SHGC values is implemented | 0.8 | 0.25 |  | 
Roof insulation | Poor roof insulation: 25% of total building heat losses Cooling savings are more than 3 times higher than the insulation on the walls Simple, easy-to-install, does not affect the daily activities | No EE insulation | 50 mm Rockwool on ceiling of all roof attic |  | 
Sealing fenestrations | ASHRAE 62.1 requirement: 0.5 ACH Malaysia requirement: 1.0 ACH | 1.8 ACH | 1.0 ACH |  | 
Daylight harvesting | Solar Heat Gain Minimization (1st scenario) Glare Protection (1st & 4th scenarios) Deep Daylight Penetration (4th scenario) Uniform Daylight Distribution (1st & 4th scenarios) | 1.8 kW | 0.9 kW |  | 
EE light | LED light | 0.9 kW | 0.45 kW |  | 
Small power improvements | Use of notebook (laptop) instead of PC, EE refrigerators/printers/TV | 1.2 KW | 0.8 KW |  | 
Heat recovery wheel for fresh air intake | Most appropriate to recover both sensible and latent heat in hot and humid climate Not a feasible EE option in a leaky building: higher infiltration into the building; condensation and mould growth problems | - | 0.5 ACH |  | 
Coefficient of Performance of ACs | Feasible and available higher COP in the market (8th & 9th scenarios) | 3.0 | 5.0 |  | 
 |  | 3.0 | 6.0 |  | 
Local climate
School terms
EE
Baseline
08

## Slide 10
Results
Simulated annual primary electricity consumption (IES-VE software)
  31,152.5 kWh
Actual annual primary electricity consumption (electricity bills)
  31,018 kWh
Chart: 
| Jan 01-31 | Feb 01-28 | Mar 01-31 | Apr 01-30 | May 01-31 | Jun 01-30 | Jul 01-31 | Aug 01-31 | Sep 01-30 | Oct 01-31 | Nov 01-30 | Dec 01-31
Simulated primary electricity consumption (kWh) | 2461.9 | 2371.6 | 2965.9 | 2754 | 2737.3 | 2721.8 | 2608.8 | 2673.4 | 2504.7 | 2463.8 | 2402.5 | 2486.7
Actual primary electricity consumption (kWh) | 2517 | 3063 | 2803 | 2875 | 2433 | 2189 | 3046 | 2688 | 2127 | 2644 | 2260 | 2373
Model validation
Validates the accuracy
0.4% Discrepancy
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 23708.5 | 3946.3 | 3497.7
Simulated annual primary electricity consumption
3. Retrofit alternatives implementation & potential energy savings
09

## Slide 11
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 30395.1 | 757.4
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 30358.7 | 793.8
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 27347.5 | 3805
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 24905.3 | 6247.2
Scenario 1: Strategy 1 - Solar Film |  | 2.4% | 30,395.1 | 757.4
Scenario 1: Strategy 1 - Solar Film |  |  |  | 
Scenario 2: Scenario 1 + Roof Insulation |  | 2.5% | 30,358.7 | 793.8
Scenario 2: Scenario 1 + Roof Insulation |  |  |  | 
Scenario 3: Scenario 2 + Seal Air Vent Louvered Windows |  | 12.2% | 27,347.5 | 3,805
Scenario 3: Scenario 2 + Seal Air Vent Louvered Windows |  |  |  | 
Scenario 4: Scenario 3 + Daylight Harvesting |  | 20.1% | 24,905.3 | 6,247.2
Scenario 4: Scenario 3 + Daylight Harvesting |  |  |  | 
Results
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 22951.1 | 3946.3 | 3497.7
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 22914.7 | 3946.3 | 3497.7
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 19.4344 | 1.9732 | 3.4977
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 19.9035 | 3.9463 | 3.4977
Scenarios
Energy saving (%)
Total Electricity (kWh)
Saving Amount (kWh)
AC electricity
Lighting electricity
Plug load electricity
The strategies conducted in IES-VE in onion model approach to reach 50% or more reduction from EE improvements to reach nZEB scenario in TADIKUM building
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 19.0708 | 0.9866 | 2.9147
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 22972.1 | 8180.4
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 19.1996 | 0.9866 | 3.4977
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 23683.9 | 7468.6
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 17.5483 | 0.9866 | 2.9147
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 21449.6 | 9702.9
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 10.529 | 0.9866 | 2.9147
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 14430.3 | 16722.2
Chart: 
| AC Electricity | Lighting Electricity | Plug Load Electricity
 | 8.7741 | 0.9866 | 2.9147
Chart: 
| Total Electricity (kWh) | Saving Amount (kWh)
 | 12675.4 | 18477.1
Scenario 5: Scenario 4 + Energy Efficient Lights |  | 24% | 23,683.9 | 7,468.6
Scenario 1: Strategy 1 - Solar Film |  |  |  | 
Scenario 6: Scenario 5 + Small Power improvements |  | 26.3% | 22,972.1 | 8,180.4
Scenario 2: Scenario 1 + Roof Insulation |  |  |  | 
Scenario 7: Scenario 6 + Heat Recovery Wheel |  | 31.1% | 21,449.6 | 9,702.9
Scenario 3: Scenario 2 + Seal Air Vent Louvered Windows |  |  |  | 
Scenario 8: Scenario 7 + Replacing AC with high COP |  | 53.7% | 14,430.3 | 16,722.2
Scenario 4: Scenario 3 + Daylight Harvesting |  |  |  | 
Scenario 9: Scenario 7 + Replacing AC with highest COP |  | 59.3% | 12,675.4 | 18,477.1
Scenario 4: Scenario 3 + Daylight Harvesting |  |  |  | 
3. Retrofit alternatives implementation & potential energy savings
10

## Slide 12
Actual primary
Electricity: 31,018 kWh
EE strategies
Climate-responsive
ZEB-ready (>50%)
Scenario 8 – 53.7%
Scenario 9 – 59.3%
Most effective
Easy-to-install
The least impact on the daily activities
Electricity: 14,430.3 kWh
nZEB (75%)
Electricity: 12,675.4 kWh
Residual energy demand - Solar panels on TADIKUM building roof:
15% – ~ 10,000 kWh/year
BEI: 115.78 kWh/m2/year
BEI: 53.86 kWh/m2/year
BEI: 47.36 kWh/m2/year
Energy Independence
EE modelling
feasibility & accuracy
Local climate considerations; Modeller’s knowledge; Local achievable values of different materials; Appropriate implementation of local responsive systems; Local requirements & standards
Not purely data-driven approach; Not by default international standards’ inputs
Dos
Don’ts
Conclusion
Summary
11

## Slide 13
This study observed and proved how implementing passive design strategies and active design technologies in an old non-climate responsive building in hot and humid weather could improve its energy efficiency by almost 60% reduction in primary electricity consumption.
The strategies employed the least structural changes on the characteristics of the building envelope due to health considerations of pupils and operation conditions of the TADIKUM preschool.
Conclusion
Summary & Future work
The most effective measure:
Reduction of the building’s heat loss and infiltration through fenestrations
The higher COP implementation
High airtightness strategies should be accompanied by proper air ventilation to reduce the cooling load and prevent excessive moisture, condensation, and mould growth risks in the building
In this paper, energy-efficient retrofit strategies towards nZEB were investigated. The life cycle cost and payback period analyses for each implemented scenario will be presented in a future paper
12

## Slide 14
Authors:
Assoc. Prof. Dr. Sr Norhayati Mahyuddin
Faculty of Built Environment
Universiti Malaya
hayati@um.edu.my
Mozhgan Samzadeh
Faculty of Built Environment
Universiti Malaya
mozhgan.s@um.edu.my
Grant number: IIRG015A-2019
1
2
3
Thank you!