## Slide 1: An investigation of the operational energy and carbon savings from practicing adaptive thermal comfort theory
Rajan Rawal1, Tarjani Mehta1, Yash Shukla1 and Susan Roaf2
1Centre for Advanced Research in Building Science and Energy, CEPT University, Ahmedabad
2Institute for Sustainable Building Design, Heriot-Watt University, Edinburgh

## Slide 2
Project to lower electricity use in 2 Indian offices in Mumbai and Ahmedabad

## Slide 3
Introduction: Operational Energy Demand In Building Sector & Emissions in Building Sector
Reference :International Energy Agency (IEA) & United Nations Environment Programme (UNEP). (2022). 2022 Global Status Report for Buildings and Construction
Share of Buildings in Global Energy and Process Emissions

## Slide 4
https://en.wikipedia.org/wiki/Energy_in_India
India: Soaring Emissions – 3rd largest emitter of CO2 globally

## Slide 5
AHMEDABAD
MUMBAI
A STUDY IN OFFICES IN 2 CITIES

## Slide 6
Low-Energy Strategy: Mixed Mode: Improving Building Energy efficiency and User Thermal Comfort
Optimized Window Operations
Mechanical Ventilation
Fan Assisted Natural ventilation
Mixed Mode Ventilation
Concurrent
Change Over
Zoned
Natural Ventilation
Mechanical cooling and natural ventilation operate in the same space at the same time.
Building switches between mechanical cooling, natural ventilation and ceiling fans on a seasonal or daily basis.
Mechanical cooling and natural ventilation operate in different areas of the building.
Diagram ref: Center for the Built Environment, University of California, Berkeley ,Mixed-Mode Building Research
GHG Reduction
Controlled and Comfortable Thermal environment
Improved Ventilation Rates
Mixed Mode Types of Ventilation

## Slide 7
Involving 4 basic physical parameters and 2 assumed levels of Clothing and Activity
Humphreys. M., F. Nicol and S. Roaf (2015). Adaptive Thermal Comfort: Foundations and Analysis, London: Earthscan/Routledge. N: 978-0415691611.
Largely based on research done in Laboratories in the USA and Northern Europe in the 1950s – 1970s
PMV
Two different Standards for Measuring Thermal Comfort: US HVAC Industry Standard AHSRAE 55

## Slide 8
Two different Standards – 2ND: ADAPTIVE MODEL OF THERMAL COMFORT
THE ADAPTIVE PRINCIPLE: PEOPLE ADAPT TO THOSE TEMPERATURES THEY NORMALLY OCCUPY AND IF THEY ARE UNCOMFORTABLE THEY ACT TO RESTORE COMFORT

## Slide 9
India Model for Adaptive Comfort (IMAC):
According to the IMAC model:
Neutral Temperatures in naturally ventilated buildings in India vary from
19.6C to 28.5 C
for 30-day outdoor running mean air temperatures ranging from
12.5C to 38.5 C.
Ref: Manu, Sanyogita, Yash Shukla, Rajan Rawal, Leena E. Thomas and Richard de Dear (2016). Field studies of thermal comfort across multiple climate zones for the subcontinent: India Model for Adaptive Comfort (IMAC), Building and Environment, Vol. 98, pp. 55-70, ISSN 0360-1323.

## Slide 10
Comfort Analysis
Chart: Mumbai (Warm & Humid)
Chart: Ahmedabad (Hot & Dry)
Adaptive Comfort Band for Mixed Mode (90% (+) and 90%(-) Acceptability Limit
30 Day Running Mean of Outdoor DBT
24°C - Fixed Setpoint Temperature as per ASHRAE-55
Operating Neutral Monthly Setpoint Temperature as per the Indian Model for Adaptive Comfort
Climate Type | Duration Outside Comfort Range | Diurnal Temperature Range | Night Purging
Warm and Humid | 18% | 11°C to 32°C | Yes Possible
Hot and Dry | 55% | 8°C to 33°C | Yes Possible
Notes: Both of these charts illustrate an analysis of comfort using a 30-day running mean of outdoor dry bulb temperature overlaid with the IMAC and ASHRAE comfort bands.

## Slide 11
Methodology: Site Description & Thermal Zoning
Building Information | 
Building Type | Commercial
Location | Ahmedabad, Mumbai
Climate Zone | Hot & Dry, Warm & Humid
Orientation | E-W Longer Axis
Build- Up Area | 1287 m2
No. of Floors | G+1
Conditioned Area | 1100m2
No. of Occupants | 100 ( 0.16 person/m2)
Working Days | Mon - Fri
Operation Hours | 09:00 hrs- 19:00hrs
WWR | 40%
HVAC Type | VRF System (Air Cooled), CAV System and DOAS and Heat Recovery
Floor Height | 3.9m

## Slide 12
Base Case Modelling
Environmental Analysis
HVAC Simulation
Boundary Conditions
Building Envelope optimisation ( U-values , SHGC)
HVAC Systems – VRF System
Lighting Controls
Schedules
Window Aperture ratio
Thermal Zoning Strategies
Model parameters: Standard Compliance : ECBC
Location & Climate
Passive Strategies
Seasonal Conditioning strategies
Potential for applying Natural Ventilation
Defining acceptable Indoor Operative temperatures and Thermal Conditions
Hot & dry | Warm & Humid
Adaptive thermal Comfort Cooling Setpoints IMAC (Indian Model of Adaptive Comfort )
Mechanical ventilation
Window Operation Schedules & Strategies
Zone Operative temperature Operation Schedules
Calculated Natural ventilation
Control Algorithms
Ventilation Strategies
Operational Strategies
Zone Groups
Natural Ventilation Simulation
Window opening Factor
Cooling Load Analysis
CO2 Emissions
Comfort Assessment by IMAC 90% Acceptability Band
Energy and Comfort Assessment through Ceiling Fan usage ( EPI Base case vs. Proposed Case)
Methodology

## Slide 13
Climate Analysis: Potential For Natural Ventilation: Seasonal, Comfort Hours, & Passive Strategies
Chart: Categorisation of Strategies Based on Temperature and Humidity Thresholds : Mumbai
Chart: Categorisation of Strategies Based on Temperature and Humidity Thresholds :Ahmedabad
Notes: Climate analysis to assess the viability of low-energy cooling and ventilation, aiming to pinpoint the factors affecting mixed-mode.

## Slide 14
Ventilation Operation Strategies
Sr no | Mode | Setpoint Indoor operative Temperatures | HVAC system | HVAC Schedule | Setpoint | Window Operation Availability | Window Aperture ratio | Ceiling Fan | Air Conditioner | Thermal Comfort Model
1 | Natural ventilation | IMAC (Indian Model for Adaptive Comfort: Monthly Setpoints) | VRF | On 24/7 | Weekly Adaptive | ON | 95% | OFF | OFF | IMAC
2 | Ceiling Fan Assisted Natural ventilation. | 1.8°C Raised setpoint Temperature as per Elevated Fan Speed | VRF | On 24/7 | Weekly Adaptive | ON | 95% | working at 0.9 m/s | OFF | IMAC
3 | Change – Over Mixed Mode | IMAC | VRF | On 24/7 | Weekly Adaptive | Scheduled | 95% | OFF | Scheduled | IMAC
4 | Fully Air Conditioned | Fixed Setpoint (ASHRAE)- 24 Degrees’ | VRF | On 24/7 | Fixed | OFF | 5% | OFF | ON | IMAC
Notes: Four Simulation scenarios with variations in ventilation operation strategies were developed to inform the sizing of the HVAC equipment and systems, fixed according to the study’s baseline specification(ECBC) to ensure comparability of results.
These scenarios are focused on leveraging Natural ventilation through window control logic to regulate the window opening based on the outlined criteria and maintain comfortable indoor zone operative temperatures when the HVAC system is not yet providing conditioned air.

## Slide 15
Analysis & Observation: Natural Ventilation + Ceiling Fan : Mumbai : Warm & Humid
Window Operation: 91.9%
Window opens when:
Tzoneair > Setpoint (IMAC Range)
Tzone air > Toutside air
Availability Value = 1
Unmet Hours for Naturally Ventilated Space - 38%
Degree of Discomfort Hours (1 to 5°C) – Observed in the NV zone We can observe that 80% of the total Unmet hours have Degree discomfort Upto 5°C.
Unmet Hours with Ceiling Fan Integration in a NV Space- 13%
(65% reduction)
Fully Open
Closed
0
1
Unmet
Met
1
0
Unmet
Met
1
0
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
ΔT: 5° C Degree Discomfort
ΔT: 1° C
ΔT:10° C Degree Discomfort

## Slide 16
Analysis & Observation: Natural Ventilation + Ceiling Fan : Ahmedabad : Hot and Dry
Fully Open
Closed
0
1
Unmet
Met
1
0
Unmet
Met
1
0
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
50% open
Window Operation: 65% (Fully Open)
Window opens when:
Tzoneair > Setpoint (IMAC Range)
Tzone air > Toutside air
Availability Value = 1
Unmet Hours for Naturally Ventilated Space - 63%
Degree of Discomfort Hours (1 to 5°C) – Observed in the NV zone - We can observe that 80% of the total Unmet hours have Degree discomfort Upto 5°C.
Unmet Hours with Ceiling Fan Integration in a NV Space- 41% (35% reduction)
ΔT: 5° C Degree Discomfort
ΔT: 1° C
ΔT:10° C Degree Discomfort

## Slide 17
Analysis & Observation: Reduction in Cooling Load (W)
Chart: Fully AC vs. Mixed Mode : Warm & Humid
Chart: Fully AC vs. Mixed Mode : Hot & Dry
Climate Type | Initial Cooling Capacity (TR) | Final Cooling Capacity (TR) | Percentage Reduction (%)
Warm and Humid | 26.74 | 24.58 | 8.07
Hot and Dry | 43.69 | 35.79 | 18.21
Notes: From the figure, we can observe that the reduction in the cooling loads observed in the Mixed Mode and fully air-conditioned Building

## Slide 18
Conclusion: Energy Performance index and Carbon Emissions
Energy Performance Index (kWh/m2.year) |  | 
Ventilation Operation Scenarios | Warm and Humid | Hot and Dry
Fully AC | 123.12 | 141.26
NV | 57.4 | 58.4
NV+ Ceiling Fan | 63.1 | 64
Mixed Mode | 87.32 | 114.98
Chart: CO2e (Tonnes)
| Fully AC | NV | NV+ Ceiling Fan | Mixed Mode
Warm and Humid | 141.2014 | 65.8298 | 72.3669 | 100.1438
Hot and Dry | 162.0055 | 66.9766 | 73.399 | 131.866
Variation in EPI observed in each scenarios
Variation in Carbon Emissions in each scenario
Notes: Optimizing building operations through Natural Ventilation (NV) and Ceiling Fans (CF) in Mixed Mode (MM) can significantly reduce energy consumption and carbon emissions in different climates. The synergy of NV and CF extends NV hours and transforms discomfort hours into comfort, offering a sustainable approach to thermal comfort.
Study reveals that adopting passive strategies alongside efficient HVAC systems can achieve substantial energy savings (18% to 29%) and reduce carbon emissions, aligning with global Net Zero targets.

## Slide 19
Thank You
S.Roaf@hw.ac.uk
Conclusion: Energy Performance index and Carbon Emissions
Using the Indian Adaptive Thermal Comfort Standards (IMAC) rather than the America ASHRAE 55 Standard enabled the studies offices to operate successfully in Natural Ventilation mode and Natural Ventilation with Fan modes for much of the year resulting in radical reductions in energy used to provide comfort and in resulting carbon emissions from the offices in both Hot Dry and Hot Humid Climates in India.
This study indicates the potential energy and CO2 emission benefits of mandating for most offices to be capable of being conditioned using mixed mode methods.

## Slide 22
0W
Analysis & Observation
Mixed Mode: Mumbai : Warm & Humid
Fully Open
Closed
0
1
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
50% open
Unmet
Met
1
0
Fig 12
Fig 13
Fig 14
Fig 12: Window Operation: 27%
Window opens when:
Tzoneair > Setpoint (IMAC Range)
Tzone air > Toutside air
Availability Value = 1
8500W
Fig 13: Hourly Variation of the Cooling Load
Fig 14: Unmet Hours: 1.14%
From the figure, we can observe that cooling loads decrease in the pre-office hours, reducing electricity consumption during that time. In the mornings, the cooling loads ranges from 0-1200W, contingent upon the degree of Window opening. The cooling load is reduced to 0W when the windows are fully open. The maximum cooling load during the summers is noted as 8340 W

## Slide 23
0W
Analysis & Observation
Mixed Mode: Ahmedabad : Hot and Dry
Fully Open
Closed
0
1
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
50% open
Unmet
Met
1
0
Fig 12a
Fig 13a
Fig 14a
Fig 12a: Window Operation: 15%
Window opens when:
Tzoneair > Setpoint (IMAC Range)
Tzone air > Toutside air
Availability Value = 1
8500W
Fig 13a: Hourly Variation of the Cooling Load
Fig 14a: Unmet Hours: 3.03%
From the figure, we can observe that cooling loads decrease in the pre-office hours, reducing electricity consumption during that time. In the mornings, the cooling loads ranges from 0-3200W, contingent upon the degree of Window opening. The cooling load is reduced to 0W when the windows are fully open. The maximum cooling load during the summers is noted as 8500 W

## Slide 24
Total Electricity Demand Of the Building
Warm and Humid
Hot and Dry
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
1
9
24
19
Hours
60 kW
Fully AC: 1.85 - 45.36 kW
Natural ventilation :0.47 - 18.56 kW
Fan Assisted NV :0.47 - 18.82 kW
Mixed Mode :0.54 - 38.25 kW
Fully AC: 1.64 - 58.21 kW
Natural ventilation :0.47 - 19.56 kW
Fan Assisted NV :0.47 - 19.92 kW
Mixed Mode :0.94 - 42.09 kW
Reduction in Peak Consumption : 48%
Reduction in Peak Consumption : 19%
Reduction in Peak Consumption: 66%
Reduction in Peak Consumption : 11%
Fig 16: Analyzing the reduction observed in total Energy Demand of the Building in both the Climate Zones
0 kW